## Instructions
GEP-OnSSET Non-GIS parameters collection & customization
This document has been put togerher in order to help with the non-GIS input parameters that are needed for the GEP-OnSSET model. Ideally, each parameter presented in the sheet "Country parameters" would be customized per country or area of interest. However, some parameters are of higher priority as they have a significant impact on the results, while others can be generalized based on regional or literature values. Below we provide some instruction on how to approach data collection.
-- Highlighted parameters: Parameters (Column "C") that are highlighted in Bold are critical for the analysis and need to be provided. Parameters that are not highlighted, may keep their default parameter (Column "F").
-- Color coding: Values (Column "D") in dark red need to be customized for each country. Values in orange, although important, can be informed by regional values (or similar e.g., per power pool). Values in black may keep their default assumption (Column "F").
For any questions of further clarification on the definition of parameters please do not hesitate to contact the modelling team. Thank you!

## Country parameters
Key Data Assumptions in GEP OnSSET v.2.0
# | Section | Parameter | Value | Unit | Default Assumption | Unit | Description | Source
1 | GIS data Selection | The list of GIS data depends on the scope of the analysis; in general ~18-22 datasets are needed for a typical OnSSET model. Documentation is available here https://gep-onsset.readthedocs.io/en/latest/GIS%20data%20collection.html
2 | Modelling period & Targets
|  | Start year | 2025 | year | 2020 | year | The start year of the analysis. Starting at the first complete year.
|  | End year | 2035 | year | 2030 | year | The end year for the results
|  | Current national electricity access rate | 33% | percentage |  |  | base year
|  | - Urban elec. rate | 50% | percentage |  |  | base year
|  | - Rural elec. rate | 10% | percentage |  |  | base year
|  | Share of population connected to the grid | 25% | percentage
|  | Share of population connected to mini-grid | 0.04% | percentage
|  | Share of population connected to SHS | 7.7% | percentage
|  | Target access rate in end year | 100% | share | 100% | share | E.g. 1 for 100% electrification rate or 0.80 for 80% electrification rate, to be achieved by the final year
3 | Population data
|  | Total population (start year) | 5731206 |  |  |  | Write the population in the base year (e.g. 2020) | 2025 National Energy Statistics Bulletin. Accra: Energy Commission. http://www.energycom.gov.gh
|  | Urban pop ratio (start year) | 0.55 |  |  |  |  | https://tradingeconomics.com/ghana/urban-population-percent-of-total-wb-data.html
|  | Rural pop ratio (start year) | 0.45
|  | Total population (end year) | 37294000 |  |  |  |  | https://population.un.org/wup/downloads
|  | Urban pop ratio (end year) | 0.633 |  |  |  |  | https://population.un.org/wup/downloads
|  | Rural pop ratio (end year) | 0.367
|  | Urban Household size | 3.3 | people/HH | 5 | people/HH | Write the number of people per household expected in urban areas | https://statsbank.statsghana.gov.gh/pxweb/en/PHC%202021%20StatsBank/PHC%202021%20StatsBank__Population/avg_hhsize_table.px/table/tableViewLayout2/
|  | Rural Household size | 4 | people/HH | 5 | people/HH | Write the number of people per household expected in rural areas | https://statsbank.statsghana.gov.gh/pxweb/en/PHC%202021%20StatsBank/PHC%202021%20StatsBank__Population/avg_hhsize_table.px/table/tableViewLayout2/
4 | Technlogy specs & costs
4.1 | Centalized Grid | Grid generating cost | 0.071 | USD/kWh | 0.1 | USD/kWh | This is the expected generating cost of electricity (USD/kWh) for the centralized grid, as expected between start-end year
|  | Expected CAPEX of new power plants | 1303 | USD/kW | 2000 | USD/kW | The cost in USD/kW to for construction of grid-connected power plants (based on the expected mix between start-end year)
|  | Annual Cap on New Grid Capacity | 140 | MW/year |  |  | Limit on new (additional) capacity that the central grid can accept per year
|  | Annual Cap on New Grid Connections | 52000 | connections/year |  |  | Limit of new connections the grid can accommodate per year
|  | Transmission losses | 3.86% | percentage | 8% | percentage | The fraction of electricity lost in transmission over the HV backbone (e.g 0.08 for 8%)
|  | Distribution losses | 31.4% | percentage | 8% | percentage | The fraction of electricity lost in distribution over the MV/LV lines (e.g 0.08 for 8%)
|  | T&D Operation & Maintenance cost | 3% |  | 3% | percentage | As a percentage of CAPEX
|  | HV line type | 330, 225, 161, 66 | kV | 66 | kV
|  | Indicative HV line cost | 53000 | USD/km | 53000 | USD/km
|  | MV line type | 11 or 33 | kV | 11 or 33 | kV
|  | Indicative MV line cost | 22000 | USD/km | 15000 | USD/km
|  | Max MV line stretch | 50 | km | 50 | km
|  | LV line type | 0.24 | kV | 0.24 | kV
|  | lv_line_cost | 12000 | USD/km | 10000 | USD/km
|  | Max LV line stretch | 0.8 | km | 0.8 | km
|  | HV to MV transformer cost | 25000 | USD/unit | 25000 | USD/unit | USD/unit (1000 kVA)
|  | MV to LV transformer cost | 10000 | USD/unit | 10000 | USD/unit | USD/unit (50 kVA)
|  | Service transformer type | 50 | kVa | 50 | kVa | kVa
|  | Max no of connections per service transformer | 300 | connections | 300 | numeric | maximum number of nodes served by each service transformer
|  | Service drop / connection cost | 100 | USD/con | 100 | USD/con | USD per connection
4.2 | Mini grids
| Diesel generator | Diesel pump price | 1.38 | USD/liter | 0.68 | USD/liter | This is the diesel price in USD/liter as expected between start-end year (note that fuel cost changes based on location) | https://goil.com.gh/new-fuel-prices/
|  | Diesel generator cost | 378 | USD/kVA | 378 | USD/kVA | USD/kVA for diesel generators
|  | Diesel generator life | 10 | years | 10 | years | Expected technology life of diesel generator (years)
|  | Diesel generator O&M cost | 10% | percentage | 10% | percentage | As percentage of CAPEX
| PV | PV module cost | 1147 | USD/kW | 1147 | USD/kW | USD/kW for solar PV panels
|  | PV panel life | 25 | years | 25 | years | Expected technology life of PV panels (years)
|  | PV O&M cost | 1.5% | percentage | 1.5% | percentage | As percentage of CAPEX
| Wind | Wind turbine cost | 2800 | USD/kW | 2800 | USD/kW | USD/kW for Wind turbine
|  | Wind turbine life | 20 | years | 20 | years | Expected technology life of Wind turbine (years)
|  | Wind turbine O&M cost | 1.5% | percentage | 1.5% | percentage | As percentage of CAPEX
| Hydro | Small scale hydro (indicative) cost | 3000 | USD/kW | 3000 | USD/kW | Mini-grid Hydro system capital cost (USD/kW) as expected in the analysis
|  | Small scale hydro life | 30 | years | 30 | years | Expected technology life of hydropower generation (years)
|  | Small scale hydro O&M cost | 1.5% | percentage | 1.5% | percentage | As percentage of CAPEX
| BoS (for mini grids) | Battery cost | 427 | USD/kWh | 427 | USD/kWh | USD/kWh of storage capacity for batteries
|  | Inverter cost | 608 | USD /kW | 608 | USD /kW | Battery inverter cost (USD /kW)
|  | Inverter life | 10 | years | 10 | years | Battery inverter life
|  | Charge/Discharge efficiency of battery | 0.92 | percentage | 0.92 | percentage
|  | Maximum depth of discharge of battery | 0.8 | percentage | 0.8 | percentage
|  | Charge controller | 142 | USD/unit | 142 | USD/Unit
|  | Maximum loss of load | 0.5% | percentage | 0.5% | percentage | Maximum loss of load allowed over the year (in share of kWh)
|  | Service drop / connection cost | 100 | USD/con | 100 | USD/con | USD per connection
|  | Distribution losses | 13.8% | percentage | 8% | percentage | The fraction of electricity lost in distribution over the MV/LV lines (e.g 0.08 for 8%)
|  | T&D Operation & Maintenance cost | 3% |  | 3% | percentage | As a percentage of CAPEX
|  | MV line type | 11 or 33 | kV | 11 or 33 | kV
|  | Indicative MV line cost | 22000 | USD/km | 15000 | USD/km
|  | LV line type | 0.24 | kV | 0.24 | kV
|  | lv_line_cost | 12000 | USD/km | 10000 | USD/km
|  | Max LV line stretch | 0.8 | km | 0.8 | km
|  | MV to LV transformer cost | 10000 | USD/unit | 10000 | USD/unit | USD/unit (50 kVA)
|  | Service transformer type | 50 | kVa | 50 | kVa | kVa
|  | Max no of connections per service transformer | 300 | connections | 300 | numeric | maximum number of nodes served by each service transformer
|  | Service drop / connection cost | 100 | USD/con | 100 | USD/con | USD per connection
4.3 | Solar Home Systems | SHS costs classification
|  | < 0.02 kW | 12000 | USD/kW | 12000 | USD/kW | Stand-alone PV capital cost (USD/kW) for household systems under 6 W
|  | 0.02-0.05 W | 9000 | USD/kW | 9000 | USD/kW | Stand-alone PV capital cost (USD/kW) for household systems between 6-30 W
|  | 0.05-0.1 W | 8000 | USD/kW | 8000 | USD/kW | Stand-alone PV capital cost (USD/kW) for household systems between 30-80 W
|  | 0.1-1 W | 6000 | USD/kW | 6000 | USD/kW | Stand-alone PV capital cost (USD/kW) for household systems between 80-200 W
|  | > 1 kW | 6000 | USD/kW | 6000 | USD/kW | Stand-alone PV capital cost (USD/kW) for household systems over 200W
|  | SHS life | 5 | years | 5 | years | Expected lifetime of stand-alone solar PV systems (years)
|  | SHS O&M | 2% | percentage | 2% | percentage | As percentage of CAPEX
4.4 | Other
|  | Discount rate - Grid | 12% | percentage | 12% | percentage | Rate used to discount CAPEX
|  | Discount rate - Grid | 12% | percentage | 12% | percentage | Rate used to discount CAPEX
|  | Discount rate - Grid | 12% | percentage | 12% | percentage | Rate used to discount CAPEX
| Solar and Wind hourly data | https://www.renewables.ninja/
| Health and Edu facilities | https://data.humdata.org/dataset/?q=Education+facilities+ghana&sort=score+desc%2C+last_modified+desc&ext_page_size=25
| grid_emission_factor | https://unfccc.int/documents/437880 | https://mybreeze.app/ef/electricity---ghana---ghana---operating-margin-grid-emission-factor---ifi---2022-01-25?utm_source=chatgpt.com
| hv_line_cost | https://www.enerdata.net/publications/daily-energy-news/gridco-starts-330-kv-power-line-linking-central-northern-ghana.html?utm_source=chatgpt.com